## NIT Data
NIT Number | Name Of Work Location | Estimated Cost | Earnest Money | Completion Period | Submission Deadline | Bid Opening Date
41/EE/E/PEED/2026-2027 | RMO Fire Alarm & Fire Fighting System at Rashtrapati Bhavan, New Delhi. | ₹ 58,63,632.00 | ₹ 1,17,273.00 | 12 Months | 13/08/2026 upto 15:00 Hrs. | 13/08/2026 upto 15:30 Hrs.

## Terms and Conditions
SECTION-II GENERAL CONDITIONS FOR SPECIALIZED ELIGIBLE AGENCIES — pages: 20, 21, 22
No. | Text
1. | The tenderer shall also be eligible to carry out himself any or all of the above specialized works without associating any specialized agency provided they fulfil the prescribed eligibility criteria for each of the above specialized work(s).In case the main contractor himself is not eligible (as per eligibility criteria) for executing any of the components of E&M work, he can directly associate the OEM/ authorized service provider of the OEM or specialized agency as per criteria mentioned for associate eligible agency. (Joint ventures are not accepted), within 7 days of issue of letter of intent/Acceptance and also after taking prior approval from the Engineer-in-charge.
2. | The intending bidder shall upload an undertaking along with the bid that "I/We shall associate specialized agencies as per the above eligibility criteria within 7 days of issue of letter of intent/Acceptance otherwise department may take action against me/us as per clause-3 of the applicable GCC of the agreement & may forfeit performance guarantee absolutely and also shall fulfil all the formalities for association of the specialized agencies as per the conditions mentioned in the " General conditions for specialized eligible agencies".
3. | The tenderer or associateagency shall submit the similar work experience documents in respect of experience of having satisfactory completed similar works as defined below during last seven years ending last day of the month previous to the one in which tenders are invited, issued by client department clearly indicating; 1. Name of Work, 2. Scope of Work, 3. Agreement No., 4. Estimated Cost, 5. Tendered Cost, 6. Final Value of Work Done, 7. Date of Start, 8. Stipulated date of Completion, 9. Actual date of completion, 10. Nature of the Work. (In case some of above said details are not mentioned in the Completion certificate, the firm shall attach sample proof in support of above details), self-attested copy of valid Electrical contractor license, GST registration of the proposed associated specialized agencies for verification (if required) and for approval of the department as per eligibility requirement mentioned in above as per FORM-II within 7(Seven) days from date of issue of Letter of Intent (LOI). Main contractor shall also be required to furnish either copy of applicable licenses/registrations or proof of applying for obtaining labour licenses, registration with EPFO, ESIC and BOCW Welfare Board of proposed associated specialized agencies along with above documents.
4. | Consent letter of such selected associated specialized agencies for association shall also be enclosed in the prescribed format as per FORM-I within 7(Seven) days along with documents.
5. | After approval of associated specialized agencies by Engineer-in-Charge, the main contractor will submit MOU signed with the Associated Specialized Agency as per FORM-III in shape of affidavit on stamp paper duly attested by notary in original within 3 (Three) Days after issue of approval letter (for Associate Specialized Agency). The MoU shall be signed by both the parties i.e. Main Contractor as 1st party and Associated Specialized Agency as 2nd party, independently for all specialized work(s).
6. | All technical discussions during currency of contract shall be attended by the Associated Specialized Agencies and the Main Contractor. Commercial/Technical submissions for the specialized work(s) shall be signed and submitted by the Associate Specialized Agencies along with the Main Contractor.
7. | The Associated Specialized Agencies and the Main Contractor shall attend the site during inspection of the work by the Engineer-in-Charge or higher authority.
8. | The Main Contractor shall be entirely responsible and answerable for all the works done by his Associated Specialized Agency regarding their quality, adherence to the laid down specification, terms and conditions, warranty/guarantee etc. as per the agreement and he shall be liable to bear any compensation that may be levied by the department under any of the clauses of the agreement.
9. | Experience gained by executing work on back-to-back contract basis is acceptable. Back-to-back contract means work awarded by owner to first agency and then by the first agency to the second agency. The first agency shall not be eligible for work experience in such a case. To get the weightage of experience, following conditions must be fulfilled. a. Work should be actually executed by the second agency with due concurrence of the owner as tri- partite agreement. It should be backed by valid agreement and experience certificate. b. Payments received by second agency should be reflected in bank accounts and income tax statements. c. Owner of the project and first agency should jointly certify the experience certificate. d. The actual amount of payment received by the second agency shall be considered for experience.
10. | In the event of the associated E&M agency not performing satisfactorily or failure of associate agency to complete the E&M work, the main contractor on written directions of the department, shall remove the Associate agency deployed on the work and shall submit proposal for approval of New associate agency without any loss of time or variation in cost to the department after completion of all formalities mentioned as above Such New associate agency shall also give an undertaking along with the main tenderer that both of them shall guarantee for the equipment already supplied for which payment has been released by the department in part. If any equipment supplied for the work, during the currency of the earlier associate agency and paid partly by the department, becomes redundant /not in a position to be installed and commissioned and put to beneficial use due to change in agency for execution of E&M work, the main contractor shall be responsible for replacement of the equipment(s) at no cost to the department. If Main Contractor wants to change the Associated Specialized Agency during the currency of the contract he shall submit name of new Associated Specialized Agency as per eligibility criteria mentioned in the NIT to execute the left over specialized work(s) after completion of all formalities mentioned as above.
11. | No change of associate agency will be allowed without prior approval of the Engineer-in-charge of the work.
12. | The main contractor shall be responsible and liable for proper and complete execution of the Electrical work and ensure coordination and completion of both civil and electrical work.
13. | Running payment for the work shall be made to the Main Contractor. In case, Main Contractor fails to make the payment to the Associated Specialized Agency(s) by him within 12 Months of receipt of each running account payment then on the written complaint of any Associated Specialized Agency(s) for such work, Engineer-in-Charge shall serve the show cause notice to Main Contractor and after considering the reply of the same he may make the payment directly to the concerned Associated Specialized Agency(s) for the work as per the terms & conditions of the agreement/MoU drawn between Main Contractor and Associated Specialized Agency(s) fixed by him, if reply of main contractor either not received or found unsatisfactory. Such payment made to the Associated Specialized Agency(s) shall be recovered by Engineer-in-Charge from the next RA/final bill due to Main Contractor as the case may be.
14. | The associate contractor shall attend the inspection of the work by the Engineer-in- charge of E&M works as and when required.
Sl.No. | Description of E&M works | Estimated cost in lacs | Minimum eligibility Criteria
1. | Maintenance of Fire Fighting System. | Rs. 19.13 Lacs | Three similar works each costing not less than 7.82 Lacs, OR
Two similar works each costing not less than 11.73 Lacs, OR
One similar work each costing not less than 15.64 Lacs,
Similar work shall mean "Maintenance of Fire Fighting System"
GENERAL TERMS AND CONDITIONS — pages: 44, 45, 46, 47, 48, 49, 50, 51, 52, 53, 54, 55, 56
No. | Text
1. | 1. Before award of work, contractor is bound to submit the following details of workers proposed to be engaged by him along with PG, failing which the tender may be cancelled and the agency will not be allowed to re-participate for the above work. It is to be noted that PG will not be accepted without the following details: - S.No. Name of worker/ Employee Category Address Qualification & Experience in case of skilled Worker Adhar No. (Photo to enclosed) Card copy be Workers/Employee Bank Details i.e. A/c No., Bank & Branch (Copy of Cancelled Cheque/photocopy of passbook to be enclosed)
2. | 2. The contractor is instructed to submit the verification form for the labour to be deployed by him during course of execution of work in Rashtrapati Bhawan. The verification form can be obtained from the O/o DCP/Sec (RB) and / or concerned JE (E). No labour will be changed without written approval of Engineer-in-charge. If any changes have been done without written approval, then no payment will be released for the changed labour.
3. | 3. The work shall be carried out at Rashtrapati Bhawan, New Delhi, the contractor is advised to quote his rates accordingly.
4. | 4. Contractor is advised to visit the site & check and go through all equipment's mentioned in Schedule of Work / Inventory / Terms & Conditions and also confirm the prevailing market rates before quoting the tender. Nothing shall be paid by Department on account of repairing / replacement of faulty & non working switch gear / component during the handover of site.
5. | 5. The rates quoted shall be inclusive of all Taxes and duties, nothing extra shall be paid on this Account.
6. | 6. If any item is to be different than whatever mentioned in the schedule of work it should specifically be brought out to the notice of department while quoting for the tender.
7. | 7. No T & P shall be issued by the department.
8. | 8. Staff provided for duty shall be professionally competent and experienced to handle the eventualities of electrical installations.
9. | 9. The agency should pay minimum salary per month including ESIC & EPFO in the bank account of employees only and bank statement of the same should be submitted along with bill as a proof of payment to the employee.
10. | 10. The firm shall abide Contractor Labour Regulations amended up to date and the payment to staff shall be made (as per Minimum Wages Act. as notified by the Govt. of India) through ECS upto 7th of each month. Beyond 7th of each month failing which the recovery will be made @ of monthly salary for each worker each day (Skilled / Unskilled). The payment to the contractor will be released only after giving proof to the department for the same with bill duly verified by AE/JE(E).
11. | 11. Wages shall be payable on the basis of actual number of working days in a month and all the workers will be eligible for one weekly off during the period of employment.
12. | 12. Staff shall be deployed for all days in a week of the month including Gazetted Holidays and National Holidays or any days of holiday. Substitute worker for the rest day and holidays shall be responsibility of the contractor and no extra claim in this regard will be entertained by the department. The quoted rates shall be inclusive of the cost of reliever for any staff. Hence service provider shall provide a reliever for any staff (whenever needed) and nothing extra shall be payable on this account.
13. | 13. All tradesmen shall be appropriately skilled to carry out their trade related works. In case no relevant trade job is available for a particular tradesman / worker during any working hour, his services may be utilized for assisting other tradesman/ or any other maintenance related job may be assigned as per the directions of Engineer-in-charge, No extra claim shall be entertained by the department on this account.
14. | 14. The contractor shall furnish Name & Contract Number and a valid email ID of the Firm and person, who should be contracted during general/emergency contact/complaint emergency.
15. | 15. No extra payment payable for wastage of labour.
16. | 16. Agency has to maintain the logbook & enter all complaint & work done at site and also maintain attendance register duly verified by JE / AE every day.
17. | 17. The operation work is being on contract in absence of permanent Technician, Operator & Khallasi, in case of deputing permanent employee by the department, the contract shall be terminated in between with a prior notice of 15 days to the contractor. In such case the payment shall be made pro-data for work done.
18. | 18. All the dismantled material if any received from site shall be returned to the department and deposited in the store of the JE(E), President Estate for which nothing extra shall be paid.
19. | 19. Department shall in no way be involved in any dispute of whatever kind, between the contractor and the staff engaged by him.
20. | 20. No staff shall leave his duty unless relieved by his relievers. Engineer in charge reserves the right to detain the staff for next shift if the reliever fails to turn up. The O.T.A applicable in this case shall be borne by the contractor.
21. | 21. The cleaning/comprehensive maintenance of system included in the list of Inventory shall be done in accordance with frequency of work, if not done necessary recovery shall be made from the bills of the contractor for which contractor shall be responsible. The recovery amount decided by the Engineer-in-charge salary final and binding on the contractor and this will not be arbitrable.
22. | 22. Any loss or damage to the inventory (as per NIT) by way of theft sabotage or mal-operation of equipment, switch gears shall be made good by the contractor.
23. | 23. Staff shall wear the uniform/dress as per the instruction of Engineer-in-Charge during duty hours at Rashtrapati Bhavan. If any of the staff found without/dress then recovery shall be made @200/- each per day from the contractor's bill.
24. | 24. Site is located in sensitive and high security & VVIP area, where movement and routes are restricted. Some restrictions may be imposed by the Security Agency on the working and for movement of labour, materials etc. The movement of trucks and vehicles shall be regulated in accordance with rules and regulations as approved by competent authority. The contractor shall be bound to follow all such restrictions/instructions and nothing extra shall be payable on this account. No claim whatsoever will be entertained by the department on account of any, restrictions (including temporary suspension of work) imposed by the security agencies in execution of work.
25. | 25. There may be some restrictions on free movement of laborers at site and restriction of working hours and the agency shall consider this fact while quoting the rates and executing the work. Photo passes if any required for worker shall be responsibility of the contractor.
26. | 26. The personal deployed at site should be well behaved having good integrity and shall follow the security protocols of Rashtrapati Bhawan. The personals found misbehaved or of doubtful integrity shall be immediately removed this site and his entry shall be banned. The contractor shall take all precautions while deploying manpower and provide suitable manpower immediately occurrence of such incidents in writing by Engineer-in-charge at his own cost.
27. | 27. The Contractor has to maintain record of all visits and inspection made by staff in a register and shall submit to Engineer-in-charge at every running account bill.
28. | 28. Log book as per standard Performa will have to be filled in by the contractor's staff. The log book shall be kept in the plant room which will be checked by the Engineer - in - charge or his authorized representative. The contractor's staff shall have to take action as per directions of Engineer - in - charge from time to time. The log book shall be supplied by the contractor free of cost as per standard Performa given by the department.
29. | 29. If any staff is on leave, the contractor shall arrange suitable substitute staff.
30. | 30. In case of absence of any staff, recovery at double of the minimum wages of that time shall be made from the contractor's bill.
31. | 31. If break down occurred due to negligence of the contractor's staff, than contractor shall have to replace / repair defective/unserviceable parts/equipment within his quoted rates. Nothing extra shall be paid by the department. If beyond reasonable delay in replacement of parts, then recovery shall be made from the bill as assessed by the Engineer in Charge.
32. | 32. No labour huts shall be allowed inside the campus of above said work. The contractor shall make his own arrangement for the stay of labour outside the campus including transportation and nothing extra shall be payable on this account.
33. | 33. The Contractor shall also be required to follow the rules & restrictions imposed on working/movement/stacking of materials by the local competent authority at all times. Nothing extra shall be payable on this account.
34. | 34. All the materials which are intended to be used in the work shall be got approved from the Engineer-in- Charge before put to work.
35. | 35. The watch and ward of the materials issued to the Contractor or installed at site shall be responsibility of the Contractor till the installations on completion are finally handed over to the Department.
36. | 36. Income Tax, GST and Labour Welfare cess will be deducted at prevailing rates from gross amount of contractor bills.
37. | 37. All the cleaning material i.e. soap, duster etc. shall be arranged by the contractor at his own cost. If cleaning of installation is found unsatisfactory at any time, a recovery of Rs. 200/- per occasion shall be made.
38. | 38. The contractor shall carryout the work at his own responsibility and risk. In case of any accident no claim hall be given to the contractor or his employee by the department.
39. | 39. The staff deputed in the work shall be contractor's liability, therefore no claim for continuous employment with the department.
40. | 40. The contractor shall replace the staff, in the event of misconduct by him.
41. | 41. The department shall not provide any store accommodation for the stores brought by the contractor or issued by the department.
42. | 42. Damage to the building during execution of work shall be made good by the contractor matching with the surrounding surface, otherwise the same shall be got done at the cost of working contractor.
43. | 43. Any damage done to the existing installations by contractor's staff shall be replaced by the contractor at his own cost and risk, to the entire satisfaction of the Engineer-in- Charge.
44. | 44. The makes of material will be as per attached list of approved makes against each item of work or as per instructions of Engineer in charge.
45. | 45. Contractor shall be responsible for conduct of staff/workers deployed at site of work.
46. | 46. The execution of the job shall be done in a workman like manner to give structurally sound and neat appearance.
47. | 47. The work shall be carried out in highly security area hence labour is to be engaged as per availability of site, no claim for idle labour will be accepted.
48. | 48. The contractor shall take all precautions for safety of the workman. If any accident/mishap occur, the department shall not be responsible for the same. Consequently, any compensation payable shall be at the contractor's cost.
49. | 49. Any malba generated due to dismantling/execution shall be cleared from the site of work immediately without any extra cost failing which same shall be done by the department and suitable recovery shall be made form the bill of the bill of the contractor.
50. | 50. The entry of labour/workers and materials into the Rashtrapati Bhawan / President Estate is through temporarily working passes by Security of Rashtrapati Bhawan and DCP Traffic Police for which contractor has to submit the details as required for issue of passes. Any type of losses due to delay and non-issue of passes/permit shall not be the responsibility of department. No claim whatever due to the above aspects shall be entertained by the department.
51. | 51. Strictly no electronic gadget like microphone, mobile phone, pen drive, camera, chip, SIM or other electronic equipment is not allowed in Rashtrapati Bhavan.
52. | 52. Any misbehavior, impersonation & security breaches caused by the labour will not be tolerable at all. The contractor shall be fully responsible for such acts of omission if any legal action is initiated by the competent authority for violating the security measures.
53. | 53. The agency has to provide the warranty for repair and replacement of product for minimum 12 months.
54. | 54. After the expiry of the contract, system will be handed over back to the department's authorized representative with all systems and equipments in 100% functional condition & with complete inventory including as updated during the currency of contract, failing which recovery will be made from contractor's final bill. The decision of Engineer in charge shall be final and binding.
S.No. | Name of worker/ Employee | Category | Address | Qualification & Experience in case of skilled Worker | Adhar No. (Photo to enclosed) | Card copy be | Workers/Employee Bank Details i.e. A/c No., Bank & Branch (Copy of Cancelled Cheque/ photocopy of passbook to be enclosed)
Assistant Engineer (E) (P) | Executive Engineer (E)
President Estate Elect. Division | President Estate Elect. Division
Rashtrapati Bhavan, New Delhi. | Rashtrapati Bhavan, New Delhi.
Special Conditions for maintenance tenders — pages: 49, 50, 51, 52, 53, 54, 55, 56
No. | Text
1. | 1. All the workers should wear proper dress i.e. Light Blue Color Shirt Full Sleeve and Navy Blue Trousers along with Leather Safety Shoe. If a worker is found without proer dress then a penalty of Rs 1000/- per case will be imposed by the deptt and will be deducted from next month bill.
2. | 2. Worker will display his name and designation along with subdivision and division name and lastly CPWD logo. His shirt should display CPWD logo on the back. Logo should be of thread knitting.
3. | 3. Contractor has to design a carry suitcase (with / without trolly) which should be capable of arranging all the necessary equipment in that suitcase AND SHOULD BE APPROVED BY THE ENGINEER IN CHARGE.
4. | 4. All the workers should be preferably below 50 years and maximum 10% of the work force can be of age more than 50 years.
5. | 5. The contractor has to submit the details of the work executed by each workman in the form of two photos i.e. before and after attending the complaint. The contractor has to employ Computer Operator for arranging all these photographs in a daily folder and monthly folder to be submitted in the form Pen-Drive to the AE concerned.
6. | 6. All the workers will come at the designated place in the morning 5 minute before the working hours and the contractor will take GI Tag photograph and submit the attendance in terms of numbers present / total number as per tender. Same exercise has to be completed just 5 minutes before closing time of working hours both the photograph will be submitted to JE concerned to the respective section.
7. | 7. If a worker found a absent without prior replacement, then a penalty of 3 times of the daily wages per day will be imposed.
8. | 8. If a worker is being replaced with prior approval, then he should come in proper dress as described as Para No. 1 & 2 and he should have qualification either more or equal to the qualification of earlier workmen.
9. | 9. It is presumed that contractor will make all the payments due to the workman through banks and if any complain of forced demand of money by the contractor or his representative is received from the workman and if contractor is found guilty then the necessary criminal case will be filed against the contractor and the firm will be banned at least for 05 years and his name will be recommended to the directorate to be banned for lifetime.
10. | 10. If the satisfaction level is reported by the resident as below good or not satisfactory then contractor will be given a chance to correct the mistake but even after the 2nd attempt the response is not satisfactory then a penalty of Rs. 5,000/- will be imposed for each such unsatisfactory work.
11. | 11. A performance appraisal form will be prepared by the department and the contractor will make a google link for the appraisal form and JE will ensure that the non-editable responses will be kept on record for at least 20 residents/ officers per inquiry and if contractor fails to get average less than 8.0 on a scale of 1 to 10 then he will be given a chance for another month to improve and if the contractor fails to improve the rating then his work will be terminated without any notice. For continuation of the work, one month time will be given to the contractor to bind up and the department to call new tender and put the agency in place. Such contractors will be debarred for 3 years for participating in such tender.
12. | 12. The contractor has to keep an eye on the balance stock of the material required for the satisfactory maintenance of the asset for which he / she has been given the job and he must order the additional stock after getting necessary approval from competent authority, if the current stock has reached to the threshold level. The purpose of this clause to maintain always a minimum balance of material in the stock.
13. | 13. The contractor will follow all the statutory provisions, guidelines, law and any other orders being issued by the Govt. from time to time and he / she will ensure that all the necessary payments and facilities are being provided as per the Govt. orders.
14. | 14. Contractor should brief all the workmen everyday morning about the security and safety protocol and also about the polite behavior which a worker is suppose to do with residence / officer.
15. | 15. If a worker is found to be chewing Gutakha, Tabacco, Paan etc. or having liquor etc. or smoking then a penalty of Rs. 5,000/- will be imposed per incident and the worker will be removed.
Maintenance of Fire-Fighting System — pages: 61, 62, 63, 64
No. | Text
1. | The firm shall submit an undertaking that they shall deploy licensed personal as required under IE Act & carry out work on Electrical panel and related Electrical works.
2. | The nature of job is very highly skilled, so the contractor has to employ highly skilled technicians/engineer for fortnightly visit/ As and when required to the system who must be well experienced in the field of Fire - Fighting system. (i) In case the contractor fail to maintained the system properly a recovery @ Rs. 5000/- per event or day shall be recovered from him. (ii) In case of non-carrying out preventive maintenance as per schedule recovery will be made from the bill of contractor @ Rs. 2000/- each per day or occasion.
3. | The department reserves the right to check control room and connected equipment for this completeness and performance as and when required. It will be responsibility of the contractor to keep the system clean and in order.
4. | The contractor shall take all precaution as per requirement of I-E rule & regulation 1959. The contractor shall be liable to pay compensation to the staff engaged by him in such cases in the event of any accident.
5. | In case of performance of work is found unsatisfactory, the Engineer-in-Charge may terminate the contract without any notice and no claim shall be allowed after the termination of contract.
6. | The technicians are required to be reported to the Engineer-In charge at scheduled time of his/her duty to ensure the smooth working of all the Fire-Fighting system equipment's or as per the instructions from Engineer in-Charge.
7. | Scope of the work for the contractor shall be as follows: - a) Cleaning/overhauling and servicing of all equipment's, performing the daily/weekly/monthly/six monthly checks as per manufacturer recommendations/ CPWD specification or as per direction of engineer-in-charge. b) The Control Room shall be managed round the clock by the contractor. In case of Fire Fighting System & gas flooding system, Remarks and observations regarding maintenance / malfunctioning of Fire Fighting system & Panel & allied services, Gas flooding system and allied accessories recorded in the log book / conveyed through message / letter shall be attended within 24 hrs. c) In above system if contractors fails, same shall be got rectified by the department at the risk and cost of the firm without entering into any correspondence and necessary recovery shall be made from the bill of the contractor. The necessary consumable materials & tool items for maintaining the system shall be arranged by the firm at their own cost and shall be kept ready at site in sufficient quantity under the scope of work for which nothing extra shall be paid. d) The staff deployed by the bidder shall carry out rectification works wherever necessary for proper and reliable operation of the Fire Fighting installation. m) Repair and replacement of flow switch, air release valve, hose reels, hose drums, hose pipes, coupling, hose cabinet & associated addressable control panel & fire accessories etc. n) Checking of all Fire Extinguishers provided at various locations for their serviceability w.r.t leakage, thorough cleaning, due date record, safety seal check, nozzle and hose pipe, hose reel, hose cabinets lock checks to keep the entire system in ready to operate state once in a quarter period. Re- filling of the fire extinguisher as per standard norms/ due date will be cover under the comprehensive maintenance and at no extra cost paid by department. o) In case of an emergency hour, if any fault occurs, the agency will have to attend/rectify the same for which no additional payment will be made by the department. p) The firms must have to maintain one First Aid Kit Box with the required medicine etc., which is to be verified by the Engineer-in-Charge or his authorized representatives on a regular basis, failing which, penal recovery @ Rs 100/-per person per month will be made from bills. q) In the event of any accident during the operation or maintenance of the equipment leading to injuries, damage to human beings, equipment, or loss of life, the contractor shall be fully responsible for the setting claims and indemnities. In this respect, no compensation shall be made by the department. r) All installations shall be kept clean and safe from the risk of fire, theft, accidents, damage etc. s) The contractor will keep the department indemnified against all losses, damage or liability arising out of or imposed in the context of the staff employment by him. t) It shall be entirely the responsibility of the contractor to ensure that no unlawful act is done by his personnel while on duty. In case any theft or loss of department property takes place due to the negligence or carelessness of his personnel, the contractor will be held responsible and shall make good the same.
Assistant Engineer (E) (P) | Executive Engineer (E)
Assistant Engineer (E) (P) | Executive Engineer (E)
President Estate Elect. Division | President Estate Elect. Division
Rashtrapati Bhavan, New Delhi. | Rashtrapati Bhavan, New Delhi.
S. No. | Work Involved
1 | Siamese connections Operational testing by arranging water from nearest available yard hydrants. External and Internal cleaning of cabinet from all sides, i/c partitions cleaning the accessories fitted inside the cabinet checking the tightness of nuts bolts change of broken glass panes, locks.
2 | Yard Hydrants Fully lock open and closing of hydrant valve, applying grease inside the female coupling, polishing of gunmetal parts, replacement/adding the asbestos gland, if required checking the tightness of nuts bolts, cleaning inside and outside the hydrant box, vertical pipe, hydrant valve, replacement of broken, glass, repair and replacement of damaged lock. Testing andChecking of pressure of water.
3 | Sprinkler system alarm bell To open the valve fully open. Test the bell, its nuts bolts, its tightness attending to leakage if any and close test valve of sprinkler alarm valve.
4 | Sprinklers sluice valve Cleaning the sluice valve. Fully closing the valve and then fully locked open the valve in its original position. Removing the lod gland packing and inserting new gland packing if required greasing, checking the tightness of nuts bolts gasket etc.
5 | Internal Hydrant Polishing of gun metal parts applying grease inside the female coupling, to open and close 2 Nos. head valves (landing valves) checking the tightness of nuts bolts, if found necessary to replace internal rubber seat gasket or flange insertion, clean the dirt and dust from valve.
6 | HoseReel Unrolling, re-rolling of hose tube, to open and close the shut off nozzle, gate valve, tighting of different clamps, nuts bolts, cleaning of complete hose reel, polishing of nozzle applying grease outside adopter.
7 | Branch pipe & Nozzle Taking outside the branch pipe from shaft (enclosure) cleaning Branch pipe nozzle and re- fixing it in its place.
8 | RRL Hoses Taking hose outside the cabinet/shaft unrolling of fire hose, dry it in sun shade dusting it with French chalks powder, polishing of a coupling, changing of spring, O"ringwhererequiredof female and coupling. re-rolling and putting it back in to shaft/cabinet/position
9 | Cabinet and shaft Cleaning of clear glasses, cleaning and dusting off the interior of shaft/cabinet complete as well as exteriors cleaning of the risers, removing the spiders web etc. & replacement of broken glasses.
10 | Air Vessel Cleaning of exterior of air vessel, draining out of accumulated water from air vessel, replacement of defective pressure gauge, maintenance, of small gate valve checking welded joint/leakage of air vessel and attending to the leakages by welding etc. as required.
11 | Cut-off valves Cleaning the sluice valve chamber, (where required) by way of removing the garbage, slit from inside the chamber. Fully closing the valve and then fully open it and lock it in its original position). Removing the old gland packing, greasing, checking the tightness of nuts bolts as required.
12 | Sprinklers examination and cleaning. Cleaning the dust and other foreign materials if any from overhead pipe line and sprinkler heads, applying polish as per requirement on sprinkler heads checking the pressure of pipe line.
13 | Nonereturnvalve To check for the leakages and to replace the gasket asrequired
14 | Drainvalve Polishing to open and close it fully, checking of leakagesetc.
S.No. | Item | Pump Room | Terrace | Various Location of Main Building | Total | Unit
1 | Wet Riser main Pump (75 HP) | 1 | 0 | 0 | 1 | No.
2 | Sprinkler Line main Pump (75 HP) | 1 | 0 | 0 | 1 | No.
3 | Deisel Pump (105 HP) | 1 | 0 | 0 | 1 | No.
4 | Jockey Pump (15 HP) | 2 | 0 | 0 | 2 | Nos.
5 | Down Commer Line Main Pump (15 HP) | 0 | 1 | 0 | 1 | No.
6 | Drain Pump (1 HP) | 1 | 0 | 0 | 1 | No.
7 | Yard haydrant | 0 | 11 | 30 | 41 | Nos.
8 | Hose Reel Drum | 0 | 0 | 3 | 3 | Nos.
9 | Hose Boxes | 0 | 11 | 30 | 41 | Nos.
10 | Hose Pipe (15 Mtr) | 0 | 22 | 60 | 82 | Nos.
11 | Branch Pipe | 2 | 3 | 3 | 8 | Nos.
MAINTENANCE JOB INVOLVED IN FIRE FIGHTING & SPRINKLERS — pages: 64
No. | Text
1 | Siamese connections Operational testing by arranging water from nearest available yard hydrants. External and Internal cleaning of cabinet from all sides, i/c partitions cleaning the accessories fitted inside the cabinet checking the tightness of nuts bolts change of broken glass panes, locks.
2 | Yard Hydrants Fully lock open and closing of hydrant valve, applying grease inside the female coupling, polishing of gunmetal parts, replacement/adding the asbestos gland, if required checking the tightness of nuts bolts, cleaning inside and outside the hydrant box, vertical pipe, hydrant valve, replacement of broken, glass, repair and replacement of damaged lock. Testing andChecking of pressure of water.
3 | Sprinkler system alarm bell To open the valve fully open. Test the bell, its nuts bolts, its tightness attending to leakage if any and close test valve of sprinkler alarm valve.
4 | Sprinklers sluice valve Cleaning the sluice valve. Fully closing the valve and then fully locked open the valve in its original position. Removing the lod gland packing and inserting new gland packing if required greasing, checking the tightness of nuts bolts gasket etc.
5 | Internal Hydrant Polishing of gun metal parts applying grease inside the female coupling, to open and close 2 Nos. head valves (landing valves) checking the tightness of nuts bolts, if found necessary to replace internal rubber seat gasket or flange insertion, clean the dirt and dust from valve.
6 | HoseReel Unrolling, re-rolling of hose tube, to open and close the shut off nozzle, gate valve, tighting of different clamps, nuts bolts, cleaning of complete hose reel, polishing of nozzle applying grease outside adopter.
7 | Branch pipe & Nozzle Taking outside the branch pipe from shaft (enclosure) cleaning Branch pipe nozzle and re- fixing it in its place.
8 | RRL Hoses Taking hose outside the cabinet/shaft unrolling of fire hose, dry it in sun shade dusting it with French chalks powder, polishing of a coupling, changing of spring, O"ringwhererequiredof female and coupling. re-rolling and putting it back in to shaft/cabinet/position
9 | Cabinet and shaft Cleaning of clear glasses, cleaning and dusting off the interior of shaft/cabinet complete as well as exteriors cleaning of the risers, removing the spiders web etc. & replacement of broken glasses.
10 | Air Vessel Cleaning of exterior of air vessel, draining out of accumulated water from air vessel, replacement of defective pressure gauge, maintenance, of small gate valve checking welded joint/leakage of air vessel and attending to the leakages by welding etc. as required.
11 | Cut-off valves Cleaning the sluice valve chamber, (where required) by way of removing the garbage, slit from inside the chamber. Fully closing the valve and then fully open it and lock it in its original position). Removing the old gland packing, greasing, checking the tightness of nuts bolts as required.
12 | Sprinklers examination and cleaning. Cleaning the dust and other foreign materials if any from overhead pipe line and sprinkler heads, applying polish as per requirement on sprinkler heads checking the pressure of pipe line.
13 | Nonereturnvalve To check for the leakages and to replace the gasket asrequired
14 | Drainvalve Polishing to open and close it fully, checking of leakagesetc.
S. No. | Work Involved
1 | Siamese connections Operational testing by arranging water from nearest available yard hydrants. External and Internal cleaning of cabinet from all sides, i/c partitions cleaning the accessories fitted inside the cabinet checking the tightness of nuts bolts change of broken glass panes, locks.
2 | Yard Hydrants Fully lock open and closing of hydrant valve, applying grease inside the female coupling, polishing of gunmetal parts, replacement/adding the asbestos gland, if required checking the tightness of nuts bolts, cleaning inside and outside the hydrant box, vertical pipe, hydrant valve, replacement of broken, glass, repair and replacement of damaged lock. Testing andChecking of pressure of water.
3 | Sprinkler system alarm bell To open the valve fully open. Test the bell, its nuts bolts, its tightness attending to leakage if any and close test valve of sprinkler alarm valve.
4 | Sprinklers sluice valve Cleaning the sluice valve. Fully closing the valve and then fully locked open the valve in its original position. Removing the lod gland packing and inserting new gland packing if required greasing, checking the tightness of nuts bolts gasket etc.
5 | Internal Hydrant Polishing of gun metal parts applying grease inside the female coupling, to open and close 2 Nos. head valves (landing valves) checking the tightness of nuts bolts, if found necessary to replace internal rubber seat gasket or flange insertion, clean the dirt and dust from valve.
6 | HoseReel Unrolling, re-rolling of hose tube, to open and close the shut off nozzle, gate valve, tighting of different clamps, nuts bolts, cleaning of complete hose reel, polishing of nozzle applying grease outside adopter.
7 | Branch pipe & Nozzle Taking outside the branch pipe from shaft (enclosure) cleaning Branch pipe nozzle and re- fixing it in its place.
8 | RRL Hoses Taking hose outside the cabinet/shaft unrolling of fire hose, dry it in sun shade dusting it with French chalks powder, polishing of a coupling, changing of spring, O"ringwhererequiredof female and coupling. re-rolling and putting it back in to shaft/cabinet/position
9 | Cabinet and shaft Cleaning of clear glasses, cleaning and dusting off the interior of shaft/cabinet complete as well as exteriors cleaning of the risers, removing the spiders web etc. & replacement of broken glasses.
10 | Air Vessel Cleaning of exterior of air vessel, draining out of accumulated water from air vessel, replacement of defective pressure gauge, maintenance, of small gate valve checking welded joint/leakage of air vessel and attending to the leakages by welding etc. as required.
11 | Cut-off valves Cleaning the sluice valve chamber, (where required) by way of removing the garbage, slit from inside the chamber. Fully closing the valve and then fully open it and lock it in its original position). Removing the old gland packing, greasing, checking the tightness of nuts bolts as required.
12 | Sprinklers examination and cleaning. Cleaning the dust and other foreign materials if any from overhead pipe line and sprinkler heads, applying polish as per requirement on sprinkler heads checking the pressure of pipe line.
13 | Nonereturnvalve To check for the leakages and to replace the gasket asrequired
14 | Drainvalve Polishing to open and close it fully, checking of leakagesetc.
S. No. | Work Involved
1 | Siamese connections Operational testing by arranging water from nearest available yard hydrants. External and Internal cleaning of cabinet from all sides, i/c partitions cleaning the accessories fitted inside the cabinet checking the tightness of nuts bolts change of broken glass panes, locks.
2 | Yard Hydrants Fully lock open and closing of hydrant valve, applying grease inside the female coupling, polishing of gunmetal parts, replacement/adding the asbestos gland, if required checking the tightness of nuts bolts, cleaning inside and outside the hydrant box, vertical pipe, hydrant valve, replacement of broken, glass, repair and replacement of damaged lock. Testing andChecking of pressure of water.
3 | Sprinkler system alarm bell To open the valve fully open. Test the bell, its nuts bolts, its tightness attending to leakage if any and close test valve of sprinkler alarm valve.
4 | Sprinklers sluice valve Cleaning the sluice valve. Fully closing the valve and then fully locked open the valve in its original position. Removing the lod gland packing and inserting new gland packing if required greasing, checking the tightness of nuts bolts gasket etc.
5 | Internal Hydrant Polishing of gun metal parts applying grease inside the female coupling, to open and close 2 Nos. head valves (landing valves) checking the tightness of nuts bolts, if found necessary to replace internal rubber seat gasket or flange insertion, clean the dirt and dust from valve.
6 | HoseReel Unrolling, re-rolling of hose tube, to open and close the shut off nozzle, gate valve, tighting of different clamps, nuts bolts, cleaning of complete hose reel, polishing of nozzle applying grease outside adopter.
7 | Branch pipe & Nozzle Taking outside the branch pipe from shaft (enclosure) cleaning Branch pipe nozzle and re- fixing it in its place.
8 | RRL Hoses Taking hose outside the cabinet/shaft unrolling of fire hose, dry it in sun shade dusting it with French chalks powder, polishing of a coupling, changing of spring, O"ringwhererequiredof female and coupling. re-rolling and putting it back in to shaft/cabinet/position
9 | Cabinet and shaft Cleaning of clear glasses, cleaning and dusting off the interior of shaft/cabinet complete as well as exteriors cleaning of the risers, removing the spiders web etc. & replacement of broken glasses.
10 | Air Vessel Cleaning of exterior of air vessel, draining out of accumulated water from air vessel, replacement of defective pressure gauge, maintenance, of small gate valve checking welded joint/leakage of air vessel and attending to the leakages by welding etc. as required.
11 | Cut-off valves Cleaning the sluice valve chamber, (where required) by way of removing the garbage, slit from inside the chamber. Fully closing the valve and then fully open it and lock it in its original position). Removing the old gland packing, greasing, checking the tightness of nuts bolts as required.
12 | Sprinklers examination and cleaning. Cleaning the dust and other foreign materials if any from overhead pipe line and sprinkler heads, applying polish as per requirement on sprinkler heads checking the pressure of pipe line.
13 | Nonereturnvalve To check for the leakages and to replace the gasket asrequired
14 | Drainvalve Polishing to open and close it fully, checking of leakagesetc.

## Acceptable Make
Value: | null
Note | 'acceptable_make' was not found anywhere in the provided document text.

## Documents to Upload
List of Documents to be scanned and uploaded within the period of bid submission — pages: 8
No. | Text
(i) | Letter of Transmittal Duly signed as given in Annexure-III
(ii) | Copy of receipt for deposition of original EMD (as given in Annexure - I) issued from division office of any Executive Engineer, CPWD. (Including NIT issuing EE/AE, CPWD) deposited in the form of lnsurance Surety Bonds, Account Payee Demand Draft, Fixed Deposit Receipt, Banker's Cheque or Bank Guarantee (For balance amount as prescribed) issued by a Commercial Bank against EMD (Bank Guarantee Format as given in Annxure-II).
(iii) | Scan copy of the original EMD
(iv) | CPWD Enlistment order of contractor wherever required as a proof of validity (This is required only for who is registered in CPWD).
(v) | Permanent Account Number (PAN) Card as issued by the Income Tax Department.
(vi) | GST RegistrationCertificate, if already obtained by the bidder. If the bidder has not obtained GST registration as applicable, then such a case bidder shall furnish undertaking as given in Annxure- IV
(vii) | Financial information as given in Form-A
(viii) | Banker's certificate as given in Form-B OR Net worth Certificate issued by certified Chartered Accountants as given in Form-B1
(ix) | Details of eligible similar nature of works completed during the last seven years ending on the last day of the month previous to one in which bids are invited as given in Form-C
(x) | Details of Project Under Execution as given Form 'C-1'
(xi) | Declaration of bidding capacity detail as given Form 'C-3'
(xii) | Performance report of works as given in Form-D
(xiii) | Structure & Organization as given in Form-E
(xiv) | Copy of valid electrical license. The contractors shall be allowed to participate in tender with an undertaking that they will either obtain valid electrical license at the time of execution of electrical work or associates contractors having valid electrical license of eligible class.
(xv) | Undertaking by contractor on his Letter-Head in the following format: "I/We Declare that, I/We have not been Debarred/Blacklisted by Central Government/State Government."
(xvi) | Undertaking by Contractor on his letter head in the following format: "In case, I/We become first lowest tenderer and I/We are not eligible agency as per eligibility criteria; I/We will associate eligible agency fulfilling eligibility criteria as per NIT and I/We will submit documents as required."
(xvii) | ERP training certificate issued through LMS of ERP.
Notes
* | Note:
* | a) The Postal address of Executive Engineer (E), President Estate Electrical Division, CPWDmay be noted as below for correspondence and submission of Physical documents. O/o The Executive Engineer (E), President Estate Electrical Division, CPWD, South Basement, Rashtrapati Bhavan, New Delhi-110004.
* | b) List of documents mentioned in point vii, viii, x, & xiii are not applicable for CPWD enlisted contractors of appropriate class and serial no. iv is not applicable for Non-CPWD Contractor / OEM. Therefore, Agencies shall upload separate letters that these documents are not required to be submitted by them. Uploading of these letters is mandatory otherwise system will not clear the mandatory fields.
* | c) Additional following Mandatory Documents has to be submitted alongwith Performance Guarantee by the lowest tenderer failing which EMD shall be forfeited without further intimation.
* | i. Willingness Certificate from Notifier Make (Authorized to work in New Delhi area) as per Page - 14.
* | ii. Willingness Certificate from Bosch Make (Authorized to work in New Delhi area) as per Page - 15.
* | iii. Willingness Certificate from Edward Make (Authorized to work in New Delhi area) as per Page - 16.

## Schedule of Quantity
SCHEDULE OF QUANTITY — pages: 66
Sl.No. | Bhavan).\nDescription of Items | Qty |  | Rate | Unit | Amount
1 | Running, Operation and Routine Maintenance of fire fighting and sprinkler system by deputing the staff as per inventory, terms and conditions attached etc. complete as required. | 12.00 | Month | 162920.00 | Per Month | 19,55,040.00
2 | Running, Operation and Routine Maintenance of fire Alarm system by deputing the staff as per inventory, terms and conditions attached etc. complete as required. | 12.00 | Month | 235308.00 | Per Month | 28,23,696.00
3 | Annual comprehensive maintenance of following intelligent addressable fire alarm/ detection & PA system installed at Main building i/c Major/Minor repairing & replacement of all defective detectors, wiring & other accessories etc with upkeep & cleaning the panels, detectors and its accessories complete (Inventory attached) as per terms & conditions enclosed as reqd.
a) | Intelligent addressable fire alarm system (Bosch, Notifier & Edward) | 12.00 | Month | 90408.00 | Per Month | 10,84,896.00

## Page Usage Report
Metric | Value
Job ID | 05f30eb7-3727-44f1-bac6-dffd869ea97f
Report generated (IST) | 2026-08-17 15:40:03
Reporting month | 2026-08
Monthly page limit | 10000
Pages scanned this month (all jobs) | 382
Pages remaining this month | 9618
% of monthly limit used | 3.8
Pages scanned by this tender | 69
Tenders scanned this month | 8
Avg. pages scanned per tender this month | 47.8